## Gravity Sewer Main
CENTRAL COAST COUNCIL
CCC Building in Proximity to Water and Sewer Pipelines Procedure
AUDITING DESIGN OF BUILDING OVER WATER AND SEWER PIPELINES PROCEDURE
Project Name / Address:
WMA Number:
Design Consultant:
Item No. | Activity | Relevant Standard | Design Complies | Consultant Comments | CCC Comments
1 | General
1.1 | Do the drawings show an appropriate revision history, and is the design complete, checked and effectively ready for construction? | CCC Building in Proximity to Water and Sewer Pipelines Procedure |  |  |  | Yes
1.2 | Plan assessment fees and inspection fees have been paid prior to approval of design plans? | Section 306 Certificate |  |  |  | No
2 | Structural Design |  |  |  |  | Partial
2.1 | Required clearance from structure to Council easement is achieved. Category 1, 2 and 4 structures not permitted to be built over or in close proximity to Council easements. | CCC Building in Proximity to Water and Sewer Pipelines Procedure
2.2 | Are all sewers offset from all structures as per the policy? (located minimum 900mm from screw piles, 600mm from foundations). | CCC Building in Proximity to Water and Sewer Pipelines Procedure
2.3 | Where a proposal to build over or within 0.5m clearance to the face of the sewer main a sewer is conditionally accepted by Council, CCTV inspection has been noted as required on the plans. | CCC Building in Proximity to Water and Sewer Pipelines Procedure
2.4 | Relining has been noted as a condition as the structure is within the minimum clearance requirements for relining of AC / VC mains | CCC Building in Proximity to Water and Sewer Pipelines Procedure
2.5 | A plan view drawing has been provided showing any existing sewer and associated maintenance holes / junctions in relation to the proposed structure. Zone of influence shown on the plan view drawing. | CCC Building in Proximity to Water and Sewer Pipelines Procedure
2.6 | Section view drawing provided with dimensions shown, including: 1. Vertical Depth to obvert of pipe 2. Sewer / water main minimum trench width shown 3. Minimum 150mm vertical distance between invert of pipe and bottom of ZOI 4. Horizontal distance between proposed pier and face of pipe 5. Horizontal distance of zone of influence 6. 2:1 Zone of influence shown (Refer to drawing below) | CCC Building in Proximity to Water and Sewer Pipelines Procedure
2.7 | Is minimum cover achieved between proposed structure and pipe (minimum 450mm) | CCC Building in Proximity to Water and Sewer Pipelines Procedure
2.8 | Minimum 1.5m radial clearance surrounding maintenance holes and sewer junction I.O shown.
2.9 | Swimming Pools: If swimming pool base greater than 150mm below the zone of influence, then there are no piering requirements.
2.1 | Retaining Walls: Greater than 1m height walls require engineering, less than 1m high walls no engineering required. If retaining wall is paralell to sewer main, greater than 600mm horizontal clearance required to face of pipe. | CCC Building in Proximity to Water and Sewer Pipelines Procedure
2.9 | Structural engineer name, signature, date and certification stating "the design is adequate to support and protect the proposed structure from damage in the event that water/sewer main is excavated, or disturbance or settlement occurs within the zone of influence and in accordance with Central Coast Council’s Building in Proximity to Water and Sewer Pipelines Policy” | CCC Building in Proximity to Water and Sewer Pipelines Procedure Section 306 Conditions
3 | Geotechnical Design
3.1 | 1m additional site fill over sewer main requires Council approval. Geotechnical information provided. | CCC Building in Proximity to Water and Sewer Pipelines Procedure
3.2 | Geotechnical report provided if 1:1 angle of ZOI is proposed. | CCC Building in Proximity to Water and Sewer Pipelines Procedure
3.3 | Regrading of land immediately down slope of an existing sewer main designed with a slope no steeper than 3 (horizontal) to 1 (vertical). Steeper embankments would be permitted where the embankment is certified by a suitably experienced qualified civil, structural or geotechnical engineer and approved by Council based on the certification.
*SEE EXAMPLE SECTION AND PLAN DRAWINGS IN SEPARATE TABS

## Example Section DWG
EXAMPLE SECTION DRAWING

## Example Plan DWG
EXAMPLE PLAN DRAWING